## 1. Scope of Work

The selected contractor shall provide all personnel, equipment, materials, consumables, transportation, supervision, testing, and associated services required for:

- Groundwater prospecting and hydrogeological investigations.

- Water well drilling and construction.

- Supply and installation of casing and screens.

- Gravel packing and well development.

- Supply and installation of submersible pumping systems.

- Pumping tests and performance verification.

- Water quality sampling and reporting.

- Commissioning and handover of the completed water well.

## 2. Contractor Qualification Requirements

The Bidder shall provide:

### Corporate Documentation

- Valid commercial registration.

- Valid water well drilling license.

- Tax registration certificate.

- Health, Safety and Environment (HSE) policy.

- ISO certifications (preferred):

  - ISO 9001 Quality Management.

  - ISO 14001 Environmental Management.

  - ISO 45001 Occupational Health & Safety.

### Experience Requirements

- Minimum five (5) years proven experience in water well drilling.

- List of similar projects successfully completed during the last five years.

- References from previous clients.

- Details of drilling rigs and support equipment available for the project.

## 3. Technical Requirements

### 3.1 Groundwater Investigation

The Contractor shall:

- Identify the optimal drilling location through hydrogeological surveys.

- Utilize appropriate groundwater exploration techniques and instrumentation.

- Submit a groundwater assessment report prior to drilling operations.

### 3.2 Water Well Performance

The completed well shall:

- Deliver a minimum sustainable production rate of 20 m³/hour of fresh water.

- Be drilled to an estimated total depth between 300 m and 400 m, subject to geological conditions.

- Be designed to ensure long-term operational reliability and groundwater protection.

## 4. Drilling Methodology Requirements

The Bidder shall provide a detailed methodology including:

### A. Drilling Program

- Proposed drilling method.

- Rig type and specifications.

- Planned drilling fluids and additives.

- Expected drilling duration.

### B. Well Construction Program

- Detailed casing program.

- Screen design and placement.

- Gravel pack design.

- Cementing program.

- Well head completion design.

### C. Execution Schedule

The proposal shall include estimated durations for:

- Site mobilization.

- Drilling operations.

- Casing installation.

- Screen installation.

- Gravel packing.

- Well development.

- Pump installation.

- Pumping tests.

- Demobilization.

### D. Personnel

- Project Manager.

- Drilling Supervisor.

- Hydrogeologist.

- Drilling Crew.

- HSE Officer.

- Electrical Technician.

- Mechanical Technician.

## 5. Well Construction Requirements

### Casing and Screen

The construction design shall include:

- Production casing not less than 9⅝-inch OD.

- Well screen not less than 6⅝-inch OD.

- New steel casing only.

- Corrosion-resistant materials suitable for groundwater service.

### Steel Casing Standards

Each casing section shall be:

- New and unused.

- Clearly marked by the manufacturer.

- Traceable to manufacturing records.

- Compliant with internationally recognized standards including:

  - API Standards.

  - ASTM Standards.

  - AWWA Standards.

The casing shall indicate:

- Manufacturer name.

- Pipe type.

- Size and weight.

- Specification number.

- Length.

### Joints and Connections

- Threaded or welded watertight joints.

- Properly cemented casing installation.

- Couplings manufactured in accordance with API or ASTM standards.

## 6. Groundwater Protection Requirements

The Contractor shall ensure that:

- Aquifers are protected from contamination.

- Surface contaminants are prevented from entering the well.

- Well construction complies with recognized groundwater protection standards.

- The well is designed to prevent uncontrolled discharge.

## 7. Well Development Requirements

The Contractor shall submit a detailed development program including:

- Airlifting.

- Surging.

- Pump development.

- Chemical development (if required).

The objective shall be to achieve:

- Maximum well efficiency.

- Minimum sand production.

- Stable water quality and flow rate.

## 8. Submersible Pump System

The Contractor shall provide and install:

- Submersible electric pump.

- Electric motor.

- Power cables.

- Control panel.

- Protection devices.

- Associated accessories required for operation.

### Pump Requirements

- Suitable for the designed production rate.

- Corrosion-resistant construction.

- Watertight installation.

- Continuous duty operation.

- No priming requirement.

The proposal shall include:

- Pump manufacturer.

- Pump model.

- Motor rating.

- Pump curve.

- Power requirements.

## 9. Testing Requirements

The Contractor shall perform:

### Pumping Tests

- Step Drawdown Test.

- Constant Rate Pumping Test.

- Recovery Test.

### Deliverables

- Pumping test reports.

- Drawdown analysis.

- Specific capacity calculations.

- Sustainable yield evaluation.

The Contractor shall confirm that the well achieves a minimum production rate of 20 m³/hour.

## 10. HSE Requirements

The Contractor shall maintain:

- Project-specific HSE Plan.

- Risk Assessment.

- Emergency Response Plan.

- Daily Safety Reporting.

- Incident Reporting Procedures.

All activities shall comply with internationally recognized HSE standards and industry best practices.

## 11. Technical Proposal Contents

The Technical Proposal shall include:

- Company Profile.

- Valid Licenses and Registrations.

- Relevant Experience.

- Proposed Methodology.

- Equipment List.

- Personnel Organization Chart.

- Project Schedule.

- HSE Management System.

- Quality Assurance / Quality Control Plan.

- Proposed Well Design.

- Pumping Test Program.

- Project References.

## 12. Submission Deadline

All interested companies shall submit their Technical Proposals by email no later than:

### 23 July 2026

### TECHNICAL SUBMISSION EMAIL:  operations.spt@nwd.ly

COMMERCIAL SUBMISSION EMAIL:   waterwell@nwd.ly

Late submissions may not be considered.